# Enhancing the Performance of Dry Air-Cooled Systems with Wet Geothermal Cooling in Saudi Arabia

Mahmoud Bady, PhD, Mechanical Engineering Department, The Islamic University of Madinah, KSA

(On leave from Assiut University, Assiut 271516, Egypt)

Nabil A.S. Elminshawy, PhD, Mechanical Power Engineering Department, Port-Said University, Egypt

### Abstract

Reducing the temperature of the working fluid in the electric generation systems (gas turbine air inlet as well as steam from the steam turbines) requires an effective cooling medium. The present work is a part of a research project conducted in the Islamic University of Madinah, Saudi Arabia, to present reasonable solutions to pre-cool the inflow air to the air-cooled condensers in electric generation systems in KSA, when the ambient air temperature increases above the design air inlet temperature. An extensive amount of measurements has been carried out to investigate the effects of soil parameters on a buried earth-air heat exchanger. Among many parameters, the current research focused on investigating the effects of soil moisture contents and degree of compaction -represented by relative density- on the thermal performance of the buried heat exchanger. Results of the study show that; an average daily basis, a significant induced air temperature drop of 23.5 °C is achieved at the soil moisture content of 30 % and soil compaction of 91.17 %. Furthermore, the effectiveness of considered BEAHE is increased by about 33.34 % when the soil compaction is increased from 26.47 % to 91.17 %.

Recent Publications

- Nour M., Ahmed El-Seesy, Ali K. Abdel Rahman and Bady M. (2018) Influence of Adding Aluminum Oxide Nanoparticles to Diesterol Blends on the Combustion and Exhaust Emission Characteristics of a Diesel Engine. Experimental Thermal and Fluid Science 98: 634-644.

- Nour M., Kosaka H., Bady M., Sato S., Ali. K. Abdel Rahman, and K. Uchida (2017) Effect of ethanol/water blends addition on diesel fuel combustion in RCM and DI diesel engine”. Energy Conversion and Management 149: 228-243.

- Nour M., Kosaka H., Bady M., Sato S., Ali. K. Abdel Rahman (2017) Combustion and emission characteristics of DI diesel engine fueled by ethanol injected into the exhaust manifold". Fuel Processing Technology 164: 33-50.

- Bady M. (2017) Evaluation of Gaussian Plume Model against CFD Simulation through the Estimation of CO and NO Concentrations in an Urban Area”. American Journal of Environmental Sciences 13: 93-102.

- Ghada E., Negm A., Bady M., Suzuki M. and Mona G. (2017) Numerical and Experimental Investigations of the Impacts of Window Parameters on Indoor Natural Ventilation in a Residential Building.” Energy and Building 141: 321-332.

- Ahmed El-Seesy, Ali K. Abdel-Rahman, Bady M., and Ookawara S. (2017) Performance, Combustion, and Emission Characteristics of a Diesel Engine Fueled by Biodiesel-Diesel Mixtures with Multi-walled Carbon Nanotubes Additives." Energy Conversion and Management 135: 373-393.

Biography

Mahmoud Bady is an associated professor at the Islamic University of Madinah, KSA. He obtained his PhD in Mechanical Engineering from the University of Tokyo, Japan in 2008. He awarded the MSc and BSc degrees in 2002 and 1996 in Mechanical power engineering from Assiut University, Egypt. His areas of expertise include Air Quality, Internal combustion engines, and Renewable energy systems.

Email: mfbady@iu.edu.sa